## DEVImulti calculation
DEVImultiTM PVC / DEVImultiTM HDPE | [11 empty] | 123456789
Results table
| Cells with gray color - for data entry |  |  | Conductor resistence, Ohm/m | Ohm/m tolerance, +10…-33% | Parameters | Twin 1 line | Twin 2 lines | Single 1 line | Single 2 lines | Twin, Y-type 3 phase
|  |  |  | Rx=0,027 | +10% | Resistance, R∑ (Ohm/m)
| Calculation data |  |  |  |  | Linear output, p (W/m)
| Length of pipe | 150 | m |  |  | Length of cable, L (m)
| Heat loss of pipe, q | 10 | W/m |  |  | Real safety factor
| Type of cable | DEVImulti_PVC |  |  |  | Total output, P (W)
| Voltage | 220 | V |  |  | Coupling diagrams
| Safety factor | 1.3 | recommended 1,3 |  | -33% | Resistance, R∑ (Ohm/m) |  |  |  | 0.081
| Type of installation | In water pipe (enclosed by water), max. 30 W/m |  |  |  | Linear output, p (W/m) |  |  |  | 6.6392
[6 empty] | Length of cable, L (m) |  |  |  | 300
| Calculation |  |  |  |  | Real safety factor |  |  |  | 1.3278
| Linear output, 1 line instalation, p1 (with safety factor) | 13 | W/m |  |  | Total output, P (W) |  |  |  | 1991.7695
| Linear output, 2 lines instalation, p2 (with safety factor) | 6.5 | W/m |  |  | Coupling diagrams
|  |  |  | Rx=0,22 | +10% | Resistance, R∑ (Ohm/m)
| Real linear resistance, r1 | 0.16547 | Ohm/m |  |  | Linear output, p (W/m)
| Real linear resistance, r2 | 0.082735 | Ohm/m |  |  | Length of cable, L (m)
Real safety factor
Total output, P (W)
Coupling diagrams
[5 empty] | -33% | Resistance, R∑ (Ohm/m) |  |  |  | 0.0733 | 0.22
[6 empty] | Linear output, p (W/m) |  |  |  | 7.3367 | 9.7778
[6 empty] | Length of cable, L (m) |  |  |  | 300 | 150
[6 empty] | Real safety factor |  |  |  | 1.4673 | 0.97778
[6 empty] | Total output, P (W) |  |  |  | 2201.0005 | 1466.6667
Coupling diagrams
|  |  |  | Rx=2,5 | +10% | Resistance, R∑ (Ohm/m)
Linear output, p (W/m)
Length of cable, L (m)
Real safety factor
Total output, P (W)
Coupling diagrams
[5 empty] | -33% | Resistance, R∑ (Ohm/m)
Linear output, p (W/m)
Length of cable, L (m)
Real safety factor
Total output, P (W)
Coupling diagrams
|  |  |  | Technical support: EH Sales & Marketing Support |  |  | EH@danfoss.com
Coupling diagrams for 4 wire heating cable Coupling 1-10: 1 phase / 2 phase. Coupling 11: 3 phase (Y connection type). When designing and selecting the coupling method, ensure that the load is distributed equally between heat conductors as much as possible. Connection to one cable side marked “T” – twin, connection to two cable sides marked “S” – single.
Brief manual
1. Enter initial data into the gray cells:
- heat loss is entered without a safety factor;
- safety factor for electric heating systems is recommended with the value of 1,3;
- "Type of installation" determines the maximum output of one cable line for the chosen application.
2. Some calculated parameters are shown in the yellow cells.
3. "Results table" is shown with cable selection options with different coupling diagrams and types of cable installation:
- output tolerance of selection is -10%...+33%;
- the cable values are calculated, depending on 3 connection types:
power supply to one cable side - marked "T" (twin), power supply to two cable sides - marked "S" (single), 3 phase - marked "Y" (Y-type).
4. The product code should be selected with Rx value (Ohm/m) - first column of the table "Results table".
5. Find additional information in the DEVI Product Catalogue and below.
Note: It is the full responsibility of the installer/designer to use proper cold lead dimensioned for the purpose and assembly sets that establish sufficient mechanical strength, flammability resistance and water tightness - and to design the heating unit with correct output for the specific application to avoid overheating of the cable or building materials.
Note on D8: Max. 46 W/m

## Data Sheet
123456789

## Sheet2 (hidden)
Table 1
Pipe diameters
Inside pipe diameter | inch (NPS*) | 1/2 | 3/4 | 1 | =1 1/4" | 1 1/2 | 2 | 2 1/2 | 3 | 3 1/2 | 4 | 4 1/2 | 5 | 6 | 8 | 10 | 12
| mm (DN*) | 15 | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 90 | 100 | 115 | 125 | 150 | 200 | 250 | 300
Outside pipe diameter**, mm |  | 21 | 27 | 34 | 42 | 48 | 60 | 73 | 89 | 102 | 114 | 127 | 141 | 168 | 219 | 273 | 324
* NPS - Nominal Pipe Size, DN - Diameter Nominal | [17 empty] | In water pipe (enclosed by water), max. 30 W/m | 30
** Approx. value for steel pipes | [17 empty] | In concrete or without direct air contact, max. 30 W/m | 30
| Resistive cable | [8 empty] | U
| Self-limiting cable | [16 empty] | DEVImulti_PVC
[10 empty] | 230 | [7 empty] | DEVImulti_HDPE
| Metal | [8 empty] | 400
| Plastic | [16 empty] | Single
Twin
| DEVIreg 330 (+5 ... +45°C) | [16 empty] | In water pipe (enclosed by water), max. 30 W/m | 30
| ECtemp 330 (+5 ... +45°C) | [16 empty] | On plastic pipe under insulation, max. 10 W/m | 10
| DEVIreg 330 (-10 ... +10°C) | [16 empty] | On metal pipe under insulation, max. 20 W/m | 20
| ECtemp 330 (-10 ... +10°C) | [16 empty] | In a drain pipe, max. 15 W/m | 15
| DEVIreg 610 | [16 empty] | In concrete, max. 30 W/m | 30
ECtemp 610
DEVIreg 130
ECtemp 130
| DEVIreg Therm Control (for DHW) | [18 empty] | 0.054 | 0.44 | 10
[20 empty] | 0.108 | 0.88 | 10 | 0.027
[20 empty] | 0.081 | 0.66 | 7.5 | 0.22
[20 empty] | 0.0675 | 0.55 | 6.25 | 2.5
[20 empty] | 0.054 | 0.44 | 5
[20 empty] | 0.0405 | 0.33 | 3.75
[20 empty] | 0.036 | 0.2933 | 3.333
[20 empty] | 0.027 | 0.22 | 2.5
[20 empty] | 0.0135 | 0.11 | 1.25
[20 empty] | 0.009 | 0.0733 | 0.8333
[20 empty] | 0.00675 | 0.055 | 0.625

## Sheet3 (hidden)
Table 2
Output of heating cables at 230/400 V
Factory manufacturer | Resistive heating cable
| 6 W/m | 10 W/m | 18 W/m | 20 W/m | 9 W/m
Danfoss | - | ECflex 10T | ECflex 18T | ECflex 20T, ECbasic 20S | ECaqua 9T
DEVI | DEVIflexTM 6T | DEVIflexTM 10T, DEVIbasicTM 10S, DEVIcomfortTM 10T | DEVIflexTM 18T | DEVIflexTM 20T, DEVIbasicTM 20S | DEVIaquaTM 9T
Factory manufacturer | Self-limiting heating cable
| 10 W/m @ 10 °C | 25 W/m @ 10 °C | 33 W/m @ 10 °C | 7 W/m @ 45 °C | 9 W/m @ 55 °C | 12 W/m @ 70 °C
Danfoss | ECpipeguard 10, EСpipeheat 10 | ECpipeguard 25 | ECpipeguard 33 | EChotwatt 45 | EChotwatt 55 | EChotwatt 70
DEVI | DEVIpipeguardTM 10, DEVIpipeheatTM 10 | DEVIpipeguardTM 25 | DEVIpipeguardTM 33 | DEVIhotwattTM 45 | DEVIhotwattTM 55 | DEVIhotwattTM 70
Note. If a voltage of 220 V, use the coefficient 0,915 for cable output
230/400 V
DEVIflex 6T | 6 | W/m |  | ECpipeguard 10 | 10 | W/m (@ 10 °C) | DEVIflex 6T | 6 | W/m
ECflex 10T | 10 | W/m |  | EСpipeheat 10 | 10 | W/m (@ 10 °C) | ECflex 10T | 10 | W/m
DEVIflex 10T | 10 | W/m |  | ECpipeguard 25 | 25 | W/m (@ 10 °C) | DEVIflex 10T | 10 | W/m
DEVIbasic 10S | 10 | W/m |  | DEVIpipeguard 25 | 25 | W/m (@ 10 °C) | DEVIbasic 10S | 10 | W/m
DEVIcomfort 10T | 10 | W/m |  | ECpipeguard 33 | 33 | W/m (@ 10 °C) | DEVIcomfort 10T | 10 | W/m
ECflex 18T | 18 | W/m |  | DEVIpipeguard 33 | 33 | W/m (@ 10 °C) | ECaqua 9T | 9 | W/m
DEVIflex 18T | 18 | W/m |  | EChotwatt 45 | 7 | W/m (@ 45 °C) | DEVIaqua 9T | 9 | W/m
DEVIflex 20T | 20 | W/m |  | DEVIhotwatt 45 | 7 | W/m (@ 45 °C)
ECaqua 9T | 9 | W/m |  | EChotwatt 55 | 9 | W/m (@ 55 °C)
DEVIaqua 9T | 9 | W/m |  | DEVIhotwatt 55 | 9 | W/m (@ 55 °C)
|  |  |  | EChotwatt 70 | 12 | W/m (@ 70 °C)
|  |  |  | DEVIhotwatt 70 | 12 | W/m (@ 70 °C)
220/380 V
DEVIflex 6T | 5.49 | W/m |  | ECpipeguard 10 | 9.15 | W/m (@ 10 °C) | DEVIflex 6T | 5.49 | W/m
ECflex 10T | 9.15 | W/m |  | EСpipeheat 10 | 9.15 | W/m (@ 10 °C) | ECflex 10T | 9.15 | W/m
DEVIflex 10T | 9.15 | W/m |  | ECpipeguard 25 | 22.875 | W/m (@ 10 °C) | DEVIflex 10T | 9.15 | W/m
DEVIbasic 10S | 9.15 | W/m |  | DEVIpipeguard 25 | 22.875 | W/m (@ 10 °C) | DEVIbasic 10S | 9.15 | W/m
DEVIcomfort 10T | 9.15 | W/m |  | ECpipeguard 33 | 30.195 | W/m (@ 10 °C) | DEVIcomfort 10T | 9.15 | W/m
ECflex 18T | 16.47 | W/m |  | DEVIpipeguard 33 | 30.195 | W/m (@ 10 °C) | ECaqua 9T | 8.235 | W/m
DEVIflex 18T | 16.47 | W/m |  | EChotwatt 45 | 6.405 | W/m (@ 45 °C) | DEVIaqua 9T | 8.235 | W/m
DEVIflex 20T | 18.3 | W/m |  | DEVIhotwatt 45 | 6.405 | W/m (@ 45 °C)
ECaqua 9T | 8.235 | W/m |  | EChotwatt 55 | 8.235 | W/m (@ 55 °C)
DEVIaqua 9T | 8.235 | W/m |  | DEVIhotwatt 55 | 8.235 | W/m (@ 55 °C)
|  |  |  | EChotwatt 70 | 10.98 | W/m (@ 70 °C)
|  |  |  | DEVIhotwatt 70 | 10.98 | W/m (@ 70 °C)
240 V
DEVIflex 6T | 6.54 | W/m |  | ECpipeguard 10 | 10.9 | W/m (@ 10 °C) | DEVIflex 6T | 6.54 | W/m
ECflex 10T | 10.9 | W/m |  | EСpipeheat 10 | 10.9 | W/m (@ 10 °C) | ECflex 10T | 10.9 | W/m
DEVIflex 10T | 10.9 | W/m |  | ECpipeguard 25 | 27.25 | W/m (@ 10 °C) | DEVIflex 10T | 10.9 | W/m
DEVIbasic 10S | 10.9 | W/m |  | DEVIpipeguard 25 | 27.25 | W/m (@ 10 °C) | DEVIbasic 10S | 10.9 | W/m
DEVIcomfort 10T | 10.9 | W/m |  | ECpipeguard 33 | 35.97 | W/m (@ 10 °C) | DEVIcomfort 10T | 10.9 | W/m
ECflex 18T | 19.62 | W/m |  | DEVIpipeguard 33 | 35.97 | W/m (@ 10 °C) | ECaqua 9T | 9.81 | W/m
DEVIflex 18T | 19.62 | W/m |  | EChotwatt 45 | 7.63 | W/m (@ 45 °C) | DEVIaqua 9T | 9.81 | W/m
DEVIflex 20T | 21.8 | W/m |  | DEVIhotwatt 45 | 7.63 | W/m (@ 45 °C)
ECaqua 9T | 9.81 | W/m |  | EChotwatt 55 | 9.81 | W/m (@ 55 °C)
DEVIaqua 9T | 9.81 | W/m |  | DEVIhotwatt 55 | 9.81 | W/m (@ 55 °C)
|  |  |  | EChotwatt 70 | 13.08 | W/m (@ 70 °C)
|  |  |  | DEVIhotwatt 70 | 13.08 | W/m (@ 70 °C)

## Sheet1 (hidden)
Resistance |  | Расчетные длины и мощности некоторых кабелей DEVImultiTM для удельных мощностей - 30, 20, 15 и 10 Вт/м
|  |  | Rx= | 0.027 | Ohm/m | [6 empty] | 10%
2.5 | [11 empty] | 1 line
0.22 |  |  | 230 |  | V |  | 400 |  | V
0.027 |  | r, Ohm/m | p, W/m | L, m | P, W | I, A | p, W/m | L, m | P, W | I, A |  | 0.05747 | 0.16547 | 0.108 | 53.21% |  | 0.08447 | 0.16547 | 0.081 | 104.3%
|  | 0.108 | 30 | 127.7778 | 3833.3333 | 16.6667 | 30 | 222.2222 | 6666.6667 | 16.6667 |  |  | T |  |  |  |  | S
| 1 |  | 20 | 156.4952 | 3129.9036 | 13.6083 | 20 | 272.1655 | 5443.3105 | 13.6083 |  | 0.13847 | 0.027 | 5.1285 |  |  | 0.08447 | 0.081 | 1.0428
|  |  | 15 | 180.7051 | 2710.576 | 11.7851 | 15 | 314.2697 | 4714.0452 | 11.7851 |  | 0.12947 | 0.036 | 3.5964 |  |  | 0.09797 | 0.0675 | 1.4514
|  |  | 10 | 221.3176 | 2213.176 | 9.6225 | 10 | 384.9002 | 3849.0018 | 9.6225 |  | 0.12497 | 0.0405 | 3.0857 |  |  | 0.15197 | 0.0135 | 11.257
|  | 0.081 | 30 | 147.5451 | 4426.3521 | 19.245 | 30 | 256.6001 | 7698.0036 | 19.245 |  | 0.11147 | 0.054 | 2.0643 |  |  | 0.15647 | 0.009 | 17.3856
| 2 |  | 20 | 180.7051 | 3614.1013 | 15.7135 | 20 | 314.2697 | 6285.3936 | 15.7135 |  | 0.05747 | 0.108 | 0.53213 |  |  | 0.15872 | 0.00675 | 23.5141
|  |  | 15 | 208.6602 | 3129.9036 | 13.6083 | 15 | 362.8874 | 5443.3105 | 13.6083
|  |  | 10 | 255.5556 | 2555.5556 | 11.1111 | 10 | 444.4444 | 4444.4444 | 11.1111
|  | 0.0675 | 30 | 161.6275 | 4848.8257 | 21.0819 | 30 | 281.0913 | 8432.7404 | 21.0819 |  | 2 lines
| 3 |  | 20 | 197.9525 | 3959.0496 | 17.2133 | 20 | 344.2652 | 6885.3037 | 17.2133
|  |  | 15 | 228.5758 | 3428.6376 | 14.9071 | 15 | 397.5232 | 5962.8479 | 14.9071 |  | 0.025265 | 0.082735 | 0.108 | -23.39% |  | 0.001735 | 0.082735 | 0.081 | 2.142%
|  |  | 10 | 279.9471 | 2799.4708 | 12.1716 | 10 | 486.8645 | 4868.645 | 12.1716 |  |  | T |  |  |  |  | S
|  | 0.054 | 30 | 180.7051 | 5421.152 | 23.5702 | 30 | 314.2697 | 9428.0904 | 23.5702 |  | 0.055735 | 0.027 | 2.0643 |  |  | 0.001735 | 0.081 | 0.02142
| 4 |  | 20 | 221.3176 | 4426.3521 | 19.245 | 20 | 384.9002 | 7698.0036 | 19.245 |  | 0.046735 | 0.036 | 1.2982 |  |  | 0.015235 | 0.0675 | 0.2257
|  |  | 15 | 255.5556 | 3833.3333 | 16.6667 | 15 | 444.4444 | 6666.6667 | 16.6667 |  | 0.042235 | 0.0405 | 1.0428 |  |  | 0.069235 | 0.0135 | 5.1285
|  |  | 10 | 312.9904 | 3129.9036 | 13.6083 | 10 | 544.3311 | 5443.3105 | 13.6083 |  | 0.028735 | 0.054 | 0.53213 |  |  | 0.073735 | 0.009 | 8.1928
|  | 0.0405 | 30 | 208.6602 | 6259.8071 | 27.2166 | 30 | 362.8874 | 10886.6211 | 27.2166 |  | 0.025265 | 0.108 | -0.23393 |  |  | 0.075985 | 0.00675 | 11.257
| 5 |  | 20 | 255.5556 | 5111.1111 | 22.2222 | 20 | 444.4444 | 8888.8889 | 22.2222
|  |  | 15 | 295.0901 | 4426.3521 | 19.245 | 15 | 513.2002 | 7698.0036 | 19.245
|  |  | 10 | 361.4101 | 3614.1013 | 15.7135 | 10 | 628.5394 | 6285.3936 | 15.7135 |  | -33%
|  | 0.036 | 30 | 221.3176 | 6639.5281 | 28.8675 | 30 | 384.9002 | 11547.0054 | 28.8675 |  | 1 line
| 6 |  | 20 | 271.0576 | 5421.152 | 23.5702 | 20 | 471.4045 | 9428.0904 | 23.5702
|  |  | 15 | 312.9904 | 4694.8553 | 20.4124 | 15 | 544.3311 | 8164.9658 | 20.4124 |  | 0.05747 | 0.16547 | 0.108 | 53.21% |  | 0.08447 | 0.16547 | 0.081 | 104.3%
|  |  | 10 | 383.3333 | 3833.3333 | 16.6667 | 10 | 666.6667 | 6666.6667 | 16.6667 |  |  | T |  |  |  |  | S
|  | 0.027 | 30 | 255.5556 | 7666.6667 | 33.3333 | 30 | 444.4444 | 13333.3333 | 33.3333 |  | 0.13847 | 0.027 | 5.1285 |  |  | 0.08447 | 0.081 | 1.0428
| 7 |  | 20 | 312.9904 | 6259.8071 | 27.2166 | 20 | 544.3311 | 10886.6211 | 27.2166 |  | 0.12947 | 0.036 | 3.5964 |  |  | 0.09797 | 0.0675 | 1.4514
|  |  | 15 | 361.4101 | 5421.152 | 23.5702 | 15 | 628.5394 | 9428.0904 | 23.5702 |  | 0.12497 | 0.0405 | 3.0857 |  |  | 0.15197 | 0.0135 | 11.257
|  |  | 10 | 442.6352 | 4426.3521 | 19.245 | 10 | 769.8004 | 7698.0036 | 19.245 |  | 0.11147 | 0.054 | 2.0643 |  |  | 0.15647 | 0.009 | 17.3856
|  | 0.0135 | 30 | 361.4101 | 10842.304 | 47.1405 | 30 | 628.5394 | 18856.1808 | 47.1405 |  | 0.05747 | 0.108 | 0.53213 |  |  | 0.15872 | 0.00675 | 23.5141
| 8 |  | 20 | 442.6352 | 8852.7041 | 38.49 | 20 | 769.8004 | 15396.0072 | 38.49
|  |  | 15 | 511.1111 | 7666.6667 | 33.3333 | 15 | 888.8889 | 13333.3333 | 33.3333
|  |  | 10 | 625.9807 | 6259.8071 | 27.2166 | 10 | 1088.6621 | 10886.6211 | 27.2166 |  | 2 lines
|  | 0.009 | 30 | 442.6352 | 13279.0562 | 57.735 | 30 | 769.8004 | 23094.0108 | 57.735 | [8 empty] | 0.081
| 9 |  | 20 | 542.1152 | 10842.304 | 47.1405 | 20 | 942.809 | 18856.1808 | 47.1405 |  | 0.025265 | 0.082735 | 0.108 | -23.39% |  | 0.001735 | 0.082735 | 0.081 | 2.142%
|  |  | 15 | 625.9807 | 9389.7107 | 40.8248 | 15 | 1088.6621 | 16329.9316 | 40.8248 |  |  | T |  |  |  |  | S
|  |  | 10 | 766.6667 | 7666.6667 | 33.3333 | 10 | 1333.3333 | 13333.3333 | 33.3333 |  | 0.055735 | 0.027 | 2.0643 |  |  | 0.001735 | 0.081 | 0.02142
|  | 0.00675 | 30 | 511.1111 | 15333.3333 | 66.6667 | 30 | 888.8889 | 26666.6667 | 66.6667 |  | 0.046735 | 0.036 | 1.2982 |  |  | 0.015235 | 0.0675 | 0.2257
| 10 |  | 20 | 625.9807 | 12519.6142 | 54.4331 | 20 | 1088.6621 | 21773.2422 | 54.4331 |  | 0.042235 | 0.0405 | 1.0428 |  |  | 0.069235 | 0.0135 | 5.1285
|  |  | 15 | 722.8203 | 10842.304 | 47.1405 | 15 | 1257.0787 | 18856.1808 | 47.1405 |  | 0.028735 | 0.054 | 0.53213 |  |  | 0.073735 | 0.009 | 8.1928
|  |  | 10 | 885.2704 | 8852.7041 | 38.49 | 10 | 1539.6007 | 15396.0072 | 38.49 |  | 0.025265 | 0.108 | -0.23393 |  |  | 0.075985 | 0.00675 | 11.257
|  | 0.009 | 30 |  |  |  | 30 | 442.6352 | 13279.0562 | 33.1976 | 127.0171
| 11 |  | 20 |  |  |  | 20 | 542.1152 | 10842.304 | 27.1058
|  |  | 15 |  |  |  | 15 | 625.9807 | 9389.7107 | 23.4743
|  |  | 10 |  |  |  | 10 | 766.6667 | 7666.6667 | 19.1667 |  |  |  |  | -33%
[12 empty] | 0.00675 |  |  |  | 0.16547
TY
0.027
[12 empty] | 0.009 |  |  | 10%
TY
0.027

## Sheet4 (hidden)
Resistance |  | Расчетные длины и мощности некоторых кабелей DEVImultiTM для удельных мощностей - 30, 20, 15 и 10 Вт/м
|  |  | Rx= | 0.22 | Ohm/m | [6 empty] | 10%
2.5 | [11 empty] | 1 line
0.22 |  |  | 230 |  | V |  | 400 |  | V
0.027 |  | r, Ohm/m | p, W/m | L, m | P, W | I, A | p, W/m | L, m | P, W | I, A |  | 0.05453 | 0.16547 | 0.22 | -24.79% |  | 0.05547 | 0.16547 | 0.11 | 50.43%
|  | 0.88 | 30 | 44.7637 | 1342.9107 | 5.8387 | 30 | 77.8499 | 2335.4968 | 5.8387 |  |  | T |  |  |  |  | S
| 1 |  | 20 | 54.8241 | 1096.482 | 4.7673 | 20 | 95.3463 | 1906.9252 | 4.7673 |  | 0.71453 | 0.88 | -0.81197 |  |  | 0.49453 | 0.66 | -0.74929
|  |  | 15 | 63.3054 | 949.5812 | 4.1286 | 15 | 110.0964 | 1651.4456 | 4.1286 |  | 0.27453 | 0.44 | -0.62393 |  |  | 0.38453 | 0.55 | -0.69915
|  |  | 10 | 77.533 | 775.3298 | 3.371 | 10 | 134.84 | 1348.3997 | 3.371 |  | 0.16453 | 0.33 | -0.49858 |  |  | 0.05547 | 0.11 | 0.50427
|  | 0.66 | 30 | 51.6887 | 1550.6597 | 6.742 | 30 | 89.8933 | 2696.7994 | 6.742 |  | 0.12783 | 0.2933 | -0.43583 |  |  | 0.09217 | 0.0733 | 1.2574
| 2 |  | 20 | 63.3054 | 1266.1083 | 5.5048 | 20 | 110.0964 | 2201.9275 | 5.5048 |  | 0.05453 | 0.22 | -0.24786 |  |  | 0.11047 | 0.055 | 2.0085
|  |  | 15 | 73.0988 | 1096.482 | 4.7673 | 15 | 127.1283 | 1906.9252 | 4.7673
|  |  | 10 | 89.5274 | 895.2738 | 3.8925 | 10 | 155.6998 | 1556.9979 | 3.8925
|  | 0.55 | 30 | 56.6221 | 1698.6626 | 7.3855 | 30 | 98.4732 | 2954.1958 | 7.3855 |  | 2 lines
| 3 |  | 20 | 69.3476 | 1386.9522 | 6.0302 | 20 | 120.6045 | 2412.0908 | 6.0302
|  |  | 15 | 80.0757 | 1201.1358 | 5.2223 | 15 | 139.2621 | 2088.9319 | 5.2223 |  | 0.13726 | 0.082735 | 0.22 | -62.39% |  | 0.009435 | 0.082735 | 0.0733 | 12.87%
|  |  | 10 | 98.0723 | 980.7233 | 4.264 | 10 | 170.5606 | 1705.6057 | 4.264 |  |  | T |  |  |  |  | S
|  | 0.44 | 30 | 63.3054 | 1899.1625 | 8.2572 | 30 | 110.0964 | 3302.8913 | 8.2572 |  | 0.79726 | 0.88 | -0.90598 |  |  | 0.57726 | 0.66 | -0.87464
| 4 |  | 20 | 77.533 | 1550.6597 | 6.742 | 20 | 134.84 | 2696.7994 | 6.742 |  | 0.35726 | 0.44 | -0.81197 |  |  | 0.46726 | 0.55 | -0.84957
|  |  | 15 | 89.5274 | 1342.9107 | 5.8387 | 15 | 155.6998 | 2335.4968 | 5.8387 |  | 0.24726 | 0.33 | -0.74929 |  |  | 0.027265 | 0.11 | -0.24786
|  |  | 10 | 109.6482 | 1096.482 | 4.7673 | 10 | 190.6925 | 1906.9252 | 4.7673 |  | 0.21056 | 0.2933 | -0.71792 |  |  | 0.009435 | 0.0733 | 0.12872
|  | 0.33 | 30 | 73.0988 | 2192.964 | 9.5346 | 30 | 127.1283 | 3813.8504 | 9.5346 |  | 0.13726 | 0.22 | -0.62393 |  |  | 0.027735 | 0.055 | 0.50427
| 5 |  | 20 | 89.5274 | 1790.5476 | 7.785 | 20 | 155.6998 | 3113.9958 | 7.785
|  |  | 15 | 103.3773 | 1550.6597 | 6.742 | 15 | 179.7866 | 2696.7994 | 6.742 |  | -33%
|  |  | 10 | 126.6108 | 1266.1083 | 5.5048 | 10 | 220.1928 | 2201.9275 | 5.5048 |  | 1 line
|  | 0.29333 | 30 | 77.533 | 2325.9895 | 10.113 | 30 | 134.84 | 4045.1992 | 10.113
| 6 |  | 20 | 94.9581 | 1899.1625 | 8.2572 | 20 | 165.1446 | 3302.8913 | 8.2572 |  | 0.05453 | 0.16547 | 0.22 | -24.79% |  | 0.05547 | 0.16547 | 0.11 | 50.43%
|  |  | 15 | 109.6482 | 1644.723 | 7.151 | 15 | 190.6925 | 2860.3878 | 7.151 |  |  | T |  |  |  |  | S
|  |  | 10 | 134.2911 | 1342.9107 | 5.8387 | 10 | 233.5497 | 2335.4968 | 5.8387 |  | 0.71453 | 0.88 | -0.81197 |  |  | 0.49453 | 0.66 | -0.74929
|  | 0.22 | 30 | 89.5274 | 2685.8214 | 11.6775 | 30 | 155.6998 | 4670.9937 | 11.6775 |  | 0.27453 | 0.44 | -0.62393 |  |  | 0.38453 | 0.55 | -0.69915
| 7 |  | 20 | 109.6482 | 2192.964 | 9.5346 | 20 | 190.6925 | 3813.8504 | 9.5346 |  | 0.16453 | 0.33 | -0.49858 |  |  | 0.05547 | 0.11 | 0.50427
|  |  | 15 | 126.6108 | 1899.1625 | 8.2572 | 15 | 220.1928 | 3302.8913 | 8.2572 |  | 0.12783 | 0.2933 | -0.43583 |  |  | 0.09217 | 0.0733 | 1.2574
|  |  | 10 | 155.066 | 1550.6597 | 6.742 | 10 | 269.6799 | 2696.7994 | 6.742 |  | 0.05453 | 0.22 | -0.24786 |  |  | 0.11047 | 0.055 | 2.0085
|  | 0.11 | 30 | 126.6108 | 3798.325 | 16.5145 | 30 | 220.1928 | 6605.7826 | 16.5145
| 8 |  | 20 | 155.066 | 3101.3194 | 13.484 | 20 | 269.6799 | 5393.5989 | 13.484
|  |  | 15 | 179.0548 | 2685.8214 | 11.6775 | 15 | 311.3996 | 4670.9937 | 11.6775 |  | 2 lines
|  |  | 10 | 219.2964 | 2192.964 | 9.5346 | 10 | 381.385 | 3813.8504 | 9.5346 | [8 empty] | 0.0733
|  | 0.073333 | 30 | 155.066 | 4651.9791 | 20.226 | 30 | 269.6799 | 8090.3983 | 20.226 |  | 0.13726 | 0.082735 | 0.22 | -62.39% |  | 0.009435 | 0.082735 | 0.0733 | 12.87%
| 9 |  | 20 | 189.9162 | 3798.325 | 16.5145 | 20 | 330.2891 | 6605.7826 | 16.5145 |  |  | T |  |  |  |  | S
|  |  | 15 | 219.2964 | 3289.4459 | 14.3019 | 15 | 381.385 | 5720.7755 | 14.3019 |  | 0.79726 | 0.88 | -0.90598 |  |  | 0.57726 | 0.66 | -0.87464
|  |  | 10 | 268.5821 | 2685.8214 | 11.6775 | 10 | 467.0994 | 4670.9937 | 11.6775 |  | 0.35726 | 0.44 | -0.81197 |  |  | 0.46726 | 0.55 | -0.84957
|  | 0.055 | 30 | 179.0548 | 5371.6427 | 23.355 | 30 | 311.3996 | 9341.9873 | 23.355 |  | 0.24726 | 0.33 | -0.74929 |  |  | 0.027265 | 0.11 | -0.24786
| 10 |  | 20 | 219.2964 | 4385.9279 | 19.0693 | 20 | 381.385 | 7627.7007 | 19.0693 |  | 0.21056 | 0.2933 | -0.71792 |  |  | 0.009435 | 0.0733 | 0.12872
|  |  | 15 | 253.2217 | 3798.325 | 16.5145 | 15 | 440.3855 | 6605.7826 | 16.5145 |  | 0.13726 | 0.22 | -0.62393 |  |  | 0.027735 | 0.055 | 0.50427
|  |  | 10 | 310.1319 | 3101.3194 | 13.484 | 10 | 539.3599 | 5393.5989 | 13.484
|  | 0.073333 | 30 |  |  |  | 30 | 155.066 | 4651.9791 | 11.6299 | 127.0171
| 11 |  | 20 |  |  |  | 20 | 189.9162 | 3798.325 | 9.4958
|  |  | 15 |  |  |  | 15 | 219.2964 | 3289.4459 | 8.2236 |  |  | -33%
|  |  | 10 |  |  |  | 10 | 268.5821 | 2685.8214 | 6.7146 |  |  |  |  | 0.22
[14 empty] | 0.16547 |  | -24.79%
TY
0.22
10%
[14 empty] | TY |  | -24.79%
0.22

## Sheet5 (hidden)
Resistance |  | Расчетные длины и мощности некоторых кабелей DEVImultiTM для удельных мощностей - 30, 20, 15 и 10 Вт/м
|  |  | Rx= | 2.5 | Ohm/m | [6 empty] | 10%
2.5 | [11 empty] | 1 line
0.22 |  |  | 230 |  | V |  | 400 |  | V
0.027 |  | r, Ohm/m | p, W/m | L, m | P, W | I, A | p, W/m | L, m | P, W | I, A |  | 2.3345 | 0.16547 | 2.5 | -93.38% |  | 0.45953 | 0.16547 | 0.625 | -73.52%
|  | 10 | 30 | 13.2791 | 398.3717 | 1.7321 | 30 | 23.094 | 692.8203 | 1.7321 |  |  | T |  |  |  |  | S
| 1 |  | 20 | 16.2635 | 325.2691 | 1.4142 | 20 | 28.2843 | 565.6854 | 1.4142 |  | 9.8345 | 10 | -0.98345 |  |  | 7.3345 | 7.5 | -0.97794
|  |  | 15 | 18.7794 | 281.6913 | 1.2247 | 15 | 32.6599 | 489.8979 | 1.2247 |  | 4.8345 | 5 | -0.96691 |  |  | 6.0845 | 6.25 | -0.97352
|  |  | 10 | 23 | 230 | 1 | 10 | 40 | 400 | 1 |  | 3.5845 | 3.75 | -0.95587 |  |  | 1.0845 | 1.25 | -0.86762
|  | 7.5 | 30 | 15.3333 | 460 | 2 | 30 | 26.6667 | 800 | 2 |  | 3.1675 | 3.333 | -0.95035 |  |  | 0.66783 | 0.8333 | -0.80143
| 2 |  | 20 | 18.7794 | 375.5884 | 1.633 | 20 | 32.6599 | 653.1973 | 1.633 |  | 2.3345 | 2.5 | -0.93381 |  |  | 0.45953 | 0.625 | -0.73525
|  |  | 15 | 21.6846 | 325.2691 | 1.4142 | 15 | 37.7124 | 565.6854 | 1.4142
|  |  | 10 | 26.5581 | 265.5811 | 1.1547 | 10 | 46.188 | 461.8802 | 1.1547
|  | 6.25 | 30 | 16.7968 | 503.9048 | 2.1909 | 30 | 29.2119 | 876.3561 | 2.1909 |  | 2 lines
| 3 |  | 20 | 20.5718 | 411.4365 | 1.7889 | 20 | 35.7771 | 715.5418 | 1.7889
|  |  | 15 | 23.7543 | 356.3145 | 1.5492 | 15 | 41.3118 | 619.6773 | 1.5492 |  | 2.4173 | 0.082735 | 2.5 | -96.69% |  | 0.54226 | 0.082735 | 0.625 | -86.76%
|  |  | 10 | 29.093 | 290.9295 | 1.2649 | 10 | 50.5964 | 505.9644 | 1.2649 |  |  | T |  |  |  |  | S
|  | 5 | 30 | 18.7794 | 563.3826 | 2.4495 | 30 | 32.6599 | 979.7959 | 2.4495 |  | 9.9173 | 10 | -0.99173 |  |  | 7.4173 | 7.5 | -0.98897
| 4 |  | 20 | 23 | 460 | 2 | 20 | 40 | 800 | 2 |  | 4.9173 | 5 | -0.98345 |  |  | 6.1673 | 6.25 | -0.98676
|  |  | 15 | 26.5581 | 398.3717 | 1.7321 | 15 | 46.188 | 692.8203 | 1.7321 |  | 3.6673 | 3.75 | -0.97794 |  |  | 1.1673 | 1.25 | -0.93381
|  |  | 10 | 32.5269 | 325.2691 | 1.4142 | 10 | 56.5685 | 565.6854 | 1.4142 |  | 3.2503 | 3.333 | -0.97518 |  |  | 0.75056 | 0.8333 | -0.90071
|  | 3.75 | 30 | 21.6846 | 650.5382 | 2.8284 | 30 | 37.7124 | 1131.3708 | 2.8284 |  | 2.4173 | 2.5 | -0.96691 |  |  | 0.54226 | 0.625 | -0.86762
| 5 |  | 20 | 26.5581 | 531.1622 | 2.3094 | 20 | 46.188 | 923.7604 | 2.3094
|  |  | 15 | 30.6667 | 460 | 2 | 15 | 53.3333 | 800 | 2
|  |  | 10 | 37.5588 | 375.5884 | 1.633 | 10 | 65.3197 | 653.1973 | 1.633 |  | -33%
|  | 3.3333 | 30 | 23 | 690 | 3 | 30 | 40 | 1200 | 3 |  | 1 line
| 6 |  | 20 | 28.1691 | 563.3826 | 2.4495 | 20 | 48.9898 | 979.7959 | 2.4495
|  |  | 15 | 32.5269 | 487.9037 | 2.1213 | 15 | 56.5685 | 848.5281 | 2.1213 |  | 2.3345 | 0.16547 | 2.5 | -93.38% |  | 0.45953 | 0.16547 | 0.625 | -73.52%
|  |  | 10 | 39.8372 | 398.3717 | 1.7321 | 10 | 69.282 | 692.8203 | 1.7321 |  |  | T |  |  |  |  | S
|  | 2.5 | 30 | 26.5581 | 796.7434 | 3.4641 | 30 | 46.188 | 1385.6406 | 3.4641 |  | 9.8345 | 10 | -0.98345 |  |  | 7.3345 | 7.5 | -0.97794
| 7 |  | 20 | 32.5269 | 650.5382 | 2.8284 | 20 | 56.5685 | 1131.3708 | 2.8284 |  | 4.8345 | 5 | -0.96691 |  |  | 6.0845 | 6.25 | -0.97352
|  |  | 15 | 37.5588 | 563.3826 | 2.4495 | 15 | 65.3197 | 979.7959 | 2.4495 |  | 3.5845 | 3.75 | -0.95587 |  |  | 1.0845 | 1.25 | -0.86762
|  |  | 10 | 46 | 460 | 2 | 10 | 80 | 800 | 2 |  | 3.1675 | 3.333 | -0.95035 |  |  | 0.66783 | 0.8333 | -0.80143
|  | 1.25 | 30 | 37.5588 | 1126.7653 | 4.899 | 30 | 65.3197 | 1959.5918 | 4.899 |  | 2.3345 | 2.5 | -0.93381 |  |  | 0.45953 | 0.625 | -0.73525
| 8 |  | 20 | 46 | 920 | 4 | 20 | 80 | 1600 | 4
|  |  | 15 | 53.1162 | 796.7434 | 3.4641 | 15 | 92.376 | 1385.6406 | 3.4641
|  |  | 10 | 65.0538 | 650.5382 | 2.8284 | 10 | 113.1371 | 1131.3708 | 2.8284 |  | 2 lines
|  | 0.83333 | 30 | 46 | 1380 | 6 | 30 | 80 | 2400 | 6
| 9 |  | 20 | 56.3383 | 1126.7653 | 4.899 | 20 | 97.9796 | 1959.5918 | 4.899 |  | 2.4173 | 0.082735 | 2.5 | -96.69% |  | 0.54226 | 0.082735 | 0.625 | -86.76%
|  |  | 15 | 65.0538 | 975.8074 | 4.2426 | 15 | 113.1371 | 1697.0563 | 4.2426 |  |  | T |  |  |  |  | S
|  |  | 10 | 79.6743 | 796.7434 | 3.4641 | 10 | 138.5641 | 1385.6406 | 3.4641 |  | 9.9173 | 10 | -0.99173 |  |  | 7.4173 | 7.5 | -0.98897
|  | 0.625 | 30 | 53.1162 | 1593.4867 | 6.9282 | 30 | 92.376 | 2771.2813 | 6.9282 |  | 4.9173 | 5 | -0.98345 |  |  | 6.1673 | 6.25 | -0.98676
| 10 |  | 20 | 65.0538 | 1301.0765 | 5.6569 | 20 | 113.1371 | 2262.7417 | 5.6569 |  | 3.6673 | 3.75 | -0.97794 |  |  | 1.1673 | 1.25 | -0.93381
|  |  | 15 | 75.1177 | 1126.7653 | 4.899 | 15 | 130.6395 | 1959.5918 | 4.899 |  | 3.2503 | 3.333 | -0.97518 |  |  | 0.75056 | 0.8333 | -0.90071
|  |  | 10 | 92 | 920 | 4 | 10 | 160 | 1600 | 4 |  | 2.4173 | 2.5 | -0.96691 |  |  | 0.54226 | 0.625 | -0.86762
|  | 0.83333 | 30 |  |  |  | 30 | 46 | 1380 | 3.45 | 127.0171
| 11 |  | 20 |  |  |  | 20 | 56.3383 | 1126.7653 | 2.8169
|  |  | 15 |  |  |  | 15 | 65.0538 | 975.8074 | 2.4395 |  |  | -33%
|  |  | 10 |  |  |  | 10 | 79.6743 | 796.7434 | 1.9919
[14 empty] | 0.16547 |  | -93.38%
TY
2.5
10%
[14 empty] | TY |  | -93.38%
2.5